PREVENTIVE MAINTENANCE OF WATER SYSTEM (RO PLANT)

| Equipment / Instrument Code No…………………………….. Location: …………………… Done Date……………… Next due date…………… |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequency for Preventive Maintenance: Monthly, Quarterly & yearly |  |  |  |  |
| S. No. | Check Points | Standard/ Range | Observation | Action (If required) |
| 1. | Clean cartridge filter housing & change Cartridge filter (Monthly). | Cartridge filter should be changed |  |  |
| 2. | Check (Quarterly) all electrical connections for loose and burnout. | Should be Intact |  |  |
| 3. | Check (Quarterly) both pumps (Raw Water feed pump & High-pressure pump) & motor for any uneven noise and lubricate with 20W40 oil & AP3 grade grease if required. | No uneven sound |  |  |
| 4. | Check (QUARTERLY) water pipelines & tanks for any physical damages & leakages. | Should be Intact & no leakages |  |  |
| 5. | Check (QUARTERLY) flow meter for any deposition of foreign material & clean with water. | Clean & clear |  |  |
| 6. | Check (QUARTERLY) all valves for on/off operation & for any water leakages. Apply lubrication with 20W40 if found to be stiff. | Smooth operation & No leakages |  |  |
| 7. | Check all joints/valves gaskets for any water leakages & any physical damages. | No leakages &should be intact |  |  |
| 8. | Clean (YEARLY) RO membrane with chemical or A. When the pressure difference between RO inlet & reject reaches more than 1.5Kg/Cm²? B. When the product (RO water) flow is less than 510 LPH at same pressure. C. When the conductivity of product increases more than 125 µS/Cm. | Cleaning should be as per schedule |  |  |
| Entry made in the Log Book (if Applicable): - (Yes / No)_____________ Conclusion: __________________________________________________________________________ _____________________________________________________________________________________ Technician Signature with Name: User H.O.D Comments: _________________________________________________________________ Maintenance Head Comments (If Any) ____________________________________________________ USER HOD SIGNATURE………………….. MAINTENANCE HOD SIGNATURE…………… |  |  |  |  |

Preventive maintenance Checklist No.: KHPL/PMT/001                                            Revision No.: R-00