PREVENTIVE MAINTENANCE OF FIRE EXTINGUISHERS

| Equipment / Instrument Code No:- …………………….. Location: …………………… Done Date……………… Next due date…………… |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequency for Preventive Maintenance : Three Months |  |  |  |  |
| Sr. No. | Check Points | Standard/ Range | Observation | Action (If Required) |
|  | Check the position of needle indicator in pressure gauge.(Applicable to ABC type fire extinguishers only) | Should be Green zone |  |  |
|  | Check mountings nut & bolts. | Should be Tight & intact |  |  |
|  | Check nozzle obstruction. | Should be Open |  |  |
|  | Check position and condition of the locking pin. | Should be Intact |  |  |
|  | IMPORTANT: Fire extinguishers like CO, Water CO and Mechanical foam type should be refilled once in a year. | Should be Full |  |  |
|  | Check general cleaning with the help of cloth. | Should be Clean & clear |  |  |
| Entry made in the Log Book (if Applicable) :- (Yes / No)_____________ Conclusion: __________________________________________________________________________ _____________________________________________________________________________________ Technician Signature with Name:_________________________________________________________ User H.O.D Comments:_________________________________________________________________ Maintenance Head Comments (If Any)____________________________________________________ USER HOD SIGNATURE………………….. MAINTENANCE HOD SIGNATURE…………… |  |  |  |  |

Preventive maintenance Checklist No.: KHPL/PMT/007	Revision No. : R-00