PREVENTIVE MAINTENANCE OF DG SET

| Equipment / Instrument Code No…………………………….. Location: …………………… Done Date……………… Next due date…………… |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequency for Preventive Maintenance : AS per defined frequency in procedure |  |  |  |  |
| Sr. No. | Check Points | Standard/ Range | Observation | Action (If Required) |
| 1 | Check all electrical connections for loose and burnout | Should be Intact |  |  |
| B-Check |  |  |  |  |
| 2 | Change the lube oil filters, diesel filters, By pass filter and engine oil. | Should be changed properly |  |  |
| 3 | Check Air filter for dust accumulation. Clean with compressed air | Should be clean properly |  |  |
| 4 | Check the heat exchanger tank if required re-fills with coolant | Should be filled 3/4th of its total volume |  |  |
| 5 | Check fuel pumps for any leakage | Should not have any leakage |  |  |
| 6 | Check inlet and outlet pipe connection of fuel filter for any physical damage and leakage | Should not have any leakage or damage |  |  |
| 7 | Check for specific gravity electrolyte, water level and lead connector of the battery | Should be in healthy range, water level up to the cell plate and connector should be intact |  |  |
| 8 | Check inlet & Outlet cooling tower water temperature and pressure | 25– 85°C, 1 to 3 kg/cm2 |  |  |
| C-Check |  |  |  |  |
| 9 | All the points of B check & Clean the crank case breather | Should be clean properly |  |  |
| 10 | Change the air filter element | Should be changed properly |  |  |
| 11 | Clean the fuel tank & also drain the sediments | Should be clean properly |  |  |
| 12 | Adjust the valve and injectors | Should be done as per requirement |  |  |
| 13 | Check the vibration damper | No uneven damper |  |  |
| 14 | Open the head cover & adjust the clearance of tappet and also change the gasket | Should be done properly |  |  |
| 15 | Change the coolant by draining total volume | Should be changed properly |  |  |
| D-Check |  |  |  |  |
| 16 | All the points of B & C Checks and O-ring of fuel injectors and pump | Should not have any damage |  |  |
| 17 | Check the functioning of turbocharger bearing | Should be replaced if not functioning properly |  |  |
| 18 | Check the torque of turbo charger, manifold and cap screws | Should be adjusted properly |  |  |
| 19 | Overhauling the head of engine | Should be done properly |  |  |
| 20 | Check overhauling of injectors, expansion valves and pump | Should be done properly |  |  |
| 21 | Check the flow and pressure of the PT pump | Should be done properly |  |  |

Entry made in the Log Book (If Applicable): (Yes/No)

Conclusion

Technician Signature with Name:

User H.O.D. Comments:

Maintenance Head Comments (If Any)

USER HOD SIGNATURE ………………………         MAINTENANCE HOD SIGNATURE…………………

Preventive maintenance Checklist No.: KHPL/PMT/009	Revision No. : R-00