| Equipment / Instrument Code No…………………………….. Location: …………………… Done Date……………… Next due date…………… |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequency for Preventive Maintenance : Three Months |  |  |  |  |
| S. No. | Check Points | Standard/ Range | Observation | Action (If Required) |
| 1. | Check all electrical connections for loose and burnout | Should be Intact |  |  |
| 2. | Check pre filter for dust accumulation | Should be clean |  |  |
| 3. | Check the current drawing if low ampere then check the refrigerant gas level | Should be 7.5-14 Amps |  |  |
| 4. | Check the condenser/fins coil for dust accumulation. Clean using brass/nylon brush | Should be Clean to avoid high head pressure |  |  |
| 5. | Check condenser fan motor for any uneven sound / vibration | No sound and should be smoothly operated |  |  |
| 6 | Check indoor blower fan motor for smooth operation and for any uneven noise | Smoothly operated with no sound |  |  |
| 7 | Check the cooling coil for any dust accumulation | Should be properly cleaned |  |  |
| 8 | Check general cleaning with the help of cloth | Should be clean |  |  |
| 9 | Check thermostat operation desired temperature | Functioning should be proper |  |  |
| Entry made in the Log Book (if Applicable) :- (Yes / No)_____________ Conclusion: __________________________________________________________________________ _____________________________________________________________________________________ Technician Signature with Name: User H.O.D Comments:_________________________________________________________________ Maintenance Head Comments (If Any)____________________________________________________ USER HOD SIGNATURE………………….. MAINTENANCE HOD SIGNATURE…………… |  |  |  |  |

Preventive maintenance Checklist No.: KHPL/PMT/010	Revision No. : R-00